## IO_EXPANDERS
IOEX1(STRIDE SIO-MB04DAS 4CH ANALOG OUTPUT)
PIN | START | END | FUNCTION
V0 | TB.IOEX1/2.1 | TB.BL24.3 | 0-10VDC
COM0 | TB.IOEX1/2.2 | TB.BL24.4 | COM
V1 | TB.IOEX1/2.3 | TB.PMP24.3 | 0-10VDC
COM1 | TB.IOEX1/2.4 | TB.PMP24.4 | COM
V2 | TB.IOEX1/2.5 | TB.FCV134B.3 | 2-10VDC
COM2 | TB.IOEX1/2.6 | TB.FCV134B.4 | COM
V3 | TB.IOEX1/2.7 | TB.FCV205.3 | 0-10VDC
COM3 | TB.IOEX1/2.8 | TB.FCV205.4 | COM
IOEX2(STRIDE SIO-MB04DAS 4CH ANALOG OUTPUT)
PIN | START | END | FUNCTION
V0 | TB.IOEX1/2.9 | TB.FCV141.1 | 0-10VDC
COM0 | TB.IOEX1/2.10 | TB.FCV141.2 | COM
IOEX3(STRIDE SIO-MB08THMS 8CH TC/MV)
PIN | START | END | FUNCTION
V0 | TB.IOEX3.1 | TB.TC1.1 | +TT142-NGFEED
COM0 | TB.IOEX3.2 | TB.TC1.2 | -TT142-NGFEED
V1 | TB.IOEX3.3 | TB.TC1.3 | +TT301-HX406 STEAM OUT
COM1 | TB.IOEX3.4 | TB.TC1.4 | -TT301-HX406 STEAM OUT
V2 | TB.IOEX3.5 | TB.TC1.5 | +TT303-HX504 STEAM OUT
COM2 | TB.IOEX3.6 | TB.TC1.6 | -TT303-HX504 STEAM OUT
V3 | TB.IOEX3.7 | TB.TC1.7 | +TT306-EJECTOR STEAM OUT
COM3 | TB.IOEX3.8 | TB.TC1.8 | -TT306-EJECTOR STEAM OUT
V4 | TB.IOEX3.9 | TB.TC1.9 | +TT313-HX402 STEAM OUT
COM4 | TB.IOEX3.10 | TB.TC1.10 | -TT313-HX402 STEAM OUT
V5 | TB.IOEX3.11 | TB.TC1.11 | +TT319-HX402 STEAM SYSTEM
COM5 | TB.IOEX3.12 | TB.TC1.12 | -TT319-HX402 STEAM SYSTEM
V6 | TB.IOEX3/4.1 | TB.TC2.1 | +TT407-STEAM REF OUT TEMP(LREF)
COM6 | TB.IOEX3/4.2 | TB.TC2.2 | -TT407-STEAM REF OUT TEMP(LREF)
V7 | TB.IOEX3/4.3 | TB.TC2.3 | +TT408-HTS IN TEMP(LREF)
COM7 | TB.IOEX3/4.4 | TB.TC2.4 | -TT408-HTS IN TEMP(LREF)
IOEX4(STRIDE SIO-MB08THMS 8CH TC/MV)
PIN | START | END | FUNCTION
V0 | TB.IOEX3/4.5 | TB.TC2.5 | +TT410-HTS OUT TEMP(LREF)
COM0 | TB.IOEX3/4.6 | TB.TC2.6 | -TT410-HTS OUT TEMP(LREF)
V1 | TB.IOEX3/4.7 | TB.TC2.7 | +TT411-FPZ OUT TEMP(LREF)
COM1 | TB.IOEX3/4.8 | TB.TC2.8 | -TT411-FPZ OUT TEMP(LREF)
V2 | TB.IOEX3/4.9 | TB.TC2.9 | +TT430-SMR TUBES INLET TEMP
COM2 | TB.IOEX3/4.10 | TB.TC2.10 | -TT430-SMR TUBES INLET TEMP
V3 | TB.IOEX3/4.11 | TB.TC2.11 | +TT511-SILI CAR O TEMP(TYPE N TC)
COM3 | TB.IOEX3/4.12 | TB.TC2.12 | -TT511-SILI CAR O TEMP(TYPE N TC)
V4 | TB.IOEX4/5.1 | TB.TC3.1 | +TT512-SILI CAR O TEMP(TYPE N TC)
COM4 | TB.IOEX4/5.2 | TB.TC3.2 | -TT512-SILI CAR O TEMP(TYPE N TC)
V5 | TB.IOEX4/5.3 | TB.TC3.3 | +TT513-HX504 IN TEMP(BURNER)
COM5 | TB.IOEX4/5.4 | TB.TC3.4 | -TT513-HX504 IN TEMP(BURNER)
V6 | TB.IOEX4/5.5 | TB.TC3.5 | +TT514-HX504 OUT TEMP (BURNER)
COM6 | TB.IOEX4/5.6 | TB.TC3.6 | -TT514-HX504 OUT TEMP (BURNER)
V7 | TB.IOEX4/5.7 | TB.TC3.7 | +TT441- SMR TUBE 1 EXIT TEMP
COM7 | TB.IOEX4/5.8 | TB.TC3.8 | -TT441- SMR TUBE 1 EXIT TEMP
IOEX5(STRIDE SIO-MB08THMS 8CH TC/MV)
PIN | START | END | FUNCTION
V0 | TB.IOEX4/5.9 | TB.TC3.9 | +TT442-SMR TUBE 2 EXIT TEMP
COM0 | TB.IOEX4/5.10 | TB.TC3.10 | -TT442-SMR TUBE 2 EXIT TEMP
V1 | TB.IOEX4/5.11 | TB.TC3.11 | +TT443-SMR TUBE 3 EXIT TEMP
COM1 | TB.IOEX4/5.12 | TB.TC3.12 | -TT443-SMR TUBE 3 EXIT TEMP
V2 | TB.IOEX5.1 | TB.TC4.1 | +TT444-SMR TUBE 4 EXIT TEMP
COM2 | TB.IOEX5.2 | TB.TC4.2 | -TT444-SMR TUBE 4 EXIT TEMP
V3 | TB.IOEX5.3 | TB.TC4.3 | +TT445-SMR TUBE 5 EXIT TEMP
COM3 | TB.IOEX5.4 | TB.TC4.4 | -TT445-SMR TUBE 5 EXIT TEMP
V4 | TB.IOEX5.5 | TB.TC4.5 | +TT446-SMR TUBE 6 EXIT TEMP
COM4 | TB.IOEX5.6 | TB.TC4.6 | -TT446-SMR TUBE 6 EXIT TEMP
V5 | TB.IOEX5.7 | TB.TC4.7 | +TT447-SMR TUBE 7 EXIT TEMP
COM5 | TB.IOEX5.8 | TB.TC4.8 | -TT447-SMR TUBE 7 EXIT TEMP
V6 | TB.IOEX5.9 | TB.TC4.9 | +TT448-SMR TUBE 8 EXIT TEMP
COM6 | TB.IOEX5.10 | TB.TC4.10 | -TT448-SMR TUBE 8 EXIT TEMP
V7 | TB.IOEX5.11 | TB.TC4.11 | +TT449-SMR TUBE 9 EXIT TEMP
COM7 | TB.IOEX5.12 | TB.TC4.12 | -TT449-SMR TUBE 9 EXIT TEMP
IOEX6(MOXA IOLOGIK E1240 8CH ANALOG INPUT)
PIN | START | END | FUNCTION
AI0+ | TB.IOEX6/8.1 | TB.BL24.5 | BL508.AO1
AI0- | TB.IOEX6/8.2 | TB.BL24.6 | BL508.ACM
AI1+ | TB.IOEX6/8.3 | TB.PMP24.5 | PMP204.AO1
AI1- | TB.IOEX6/8.4 | TB.PMP24.6 | PMP204.ACM
AI2+ | TB.IOEX6.11 | TB.FT132.3 | FT132.FB.SIG
AI2- | TB.IOEX6.12 | TB.FT132.4 | FT132.FB.COM
AI3+ | TB.IOEX6.9 | TB.PT318.2 | PT318.FB.SIG
AI3- | TB.IOEX6.10 | 0VDC_EXT | PT318.FB.COM
AI4+ | TB.IOEX6.7 | TB.PT213.2 | PT213.FB.SIG
AI4- | TB.IOEX6.8 | 0VDC_EXT | PT213.FB.COM
AI5+ | TB.IOEX6.5 | TB.PT420.2 | PT420.FB.SIG
AI5- | TB.IOEX6.6 | 0VDC_EXT | PT420.FB.COM
AI6+ | TB.IOEX6.3 | TB.PT304.2 | PT304.FB.SIG
AI6- | TB.IOEX6.4 | 0VDC_EXT | PT304.FB.COM
AI7+ | TB.IOEX6.1 | TB.FCV134B.1 | FCV134.FB.SIG
AI7- | TB.IOEX6.2 | TB.FCV134B.2 | FCV134B.FB.COM
IOEX7(MOXA IOLOGIK E1211 16CH DIGITAL OUTPUT)
PIN | START | END | FUNCTION
DO0 | TB.IOEX7.12 | TB.DIO.LOC.8/TB.DIO.REM.6 | GRN PILOT LOCAL/REMOTE
DO1 | TB.IOEX7.11 | TB.DIO.LOC.10/TB.DIO.REM.8 | AMB PILOT LOCAL/REMOTE
DO2 | TB.IOEX7.10 | K24.XV909.A1 | XV909 CONTROL
DO3 | TB.IOEX7.9 | K24.XV501.A1 | XV501 CONTROL
GND | TB.IOEX7.8 | 0VDC_EXT | COM(SINK TYPE OUTPUTS)
DO4 | TB.IOEX7.7 | K24.XV1100.A1 | XV1100 CONTROL
DO5 | TB.IOEX7.6 | K24.XV801.A1 | XV801 CONTROL
DO6 | TB.IOEX7.5 | K24.TWV308.A1 | TWV308 CONTROL
DO7 | TB.IOEX7.4 | K24.TWV901.A1 | TWV901 CONTROL
DO8 | TB.IOEX7.3 | K24.BMM.A1 | BMM CR2 CONTROL
DO9 | TB.IOEX7.2 | TB.BL24.2 | BL508 ENABLE
DO10 | TB.IOEX7.1 | TB.PMP24.2 | PMP204 ENABLE
IOEX7(MOXA IOLOGIK E1210 16CH DIGITAL INPUT)
PIN | START | END | FUNCTION
COM0 | TB.IOEX6/8.5 | F.IOEX8 | 24VDC
DI0 | TB.IOEX6/8.6 | TB.DIO.LOC.11 | LOCAL ESTOP(NO)
DI1 | TB.IOEX6/8.7 | TB.DIO.LOC.1/TB.DIO.REM.1 | GRN BTN-LOCAL/REMOTE
DI2 | TB.IOEX6/8.8 | TB.DIO.LOC.3/TB.DIO.REM.3 | AMB BTN-LOCAL/REMOTE
GND | TB.IOEX6/8.9 | 0VDC_COM | COMMON FOR DRY TYPE CONTACTS
DI3 | TB.IOEX6/8.10 | TB.DUN.1 | DUNGS PRESSURE HIGH SWITCH
DI4 | TB.IOEX6/8.11 | TB.DUN.3 | DUNGS PRESSURE LOW SWITCH
DI5 | TB.IOEX6/8.12 | TB.DUN.5 | DUNGS PROOF OF CLOSURE SWITCH

## POWER_DISTRIBUTION
24VDC_EXT | START | END | FUNCTION
| TB.PWR3.4 | F.ECU.1 | 24VDC ECU POWER
| TB.PWR3.4 | F.ETHSW.1 | 24VDC ETH SWITCH
| TB.PWR3.4 | F.IOEX1.1 | 24VDC IOEX1
| TB.PWR3.4 | F.IOEX2.1 | 24VDC IOEX2
| TB.PWR3.4 | F.IOEX3.1 | 24VDC IOEX3
| TB.PWR3.4 | F.IOEX4.1 | 24VDC IOEX4
| TB.PWR3.4 | F.IOEX5.1 | 24VDC IOEX5
| TB.PWR3.4 | F.IOEX6.1 | 24VDC IOEX6
| TB.PWR3.4 | F.IOEX7.1 | 24VDC IOEX7
| TB.PWR3.4 | F.IOEX8.1 | 24VDC IOEX8
| TB.PWR3.4 | F.BMM24.1 | 24VDC BMM
| TB.PWR3.4 | F.XV1100.1 | 24VDC XV1100
| TB.PWR3.4 | F.XV501.1 | 24VDC XV501
| TB.PWR3.4 | F.XV909.1 | 24VDC XV909
| TB.PWR3.4 | F.COILS.1 | 24VDC RELAY COILS
| TB.PWR3.4 | F.PT.1 | 24VDC FOR Pts
| TB.PWR3.4 | F.OCI.1 | 24VDC OCI AND REG1
| TB.PWR3.4 | F.IGN | 24VDC FOR FIRE ROD
0VDC_EXT | START | END | FUNCTION
| TB.PWR3.3 | TB.PWR1.11 | 0VDC_EXT FOR IOEX1
| TB.PWR3.3 | TB.PWR1.9 | 0VDC_EXT FOR IOEX2
| TB.PWR3.3 | TB.PWR1.7 | 0VDC_EXT FOR IOEX3
| TB.PWR3.3 | TB.PWR1.5 | 0VDC_EXT FOR IOEX4
| TB.PWR3.3 | TB.PWR1.3 | 0VDC_EXT FOR IOEX5
| TB.PWR3.3 | TB.PWR1.1 | 0VDC_EXT FOR IOEX6
| TB.PWR3.3 | TB.PWR2.10 | 0VDC_EXT FOR IOEX7
| TB.PWR3.3 | TB.PWR2.7 | 0VDC_EXT FOR IOEX8
| TB.PWR3.3 | TB.PWR2.4 | 0VDC_EXT ETH SW
| TB.PWR3.3 | TB.IOEX6.4 | PT304 SIGNAL COM
| TB.PWR3.3 | TB.IOEX6.6 | PT420 SIGNAL COM
| TB.PWR3.3 | TB.IOEX6.8 | PT213 SIGNAL COM
| TB.PWR3.3 | TB.IOEX6.10 | PT318 SIGNAL COM
| TB.PWR3.3 | TB.IOEX7.8 | DIGITAL OUTPUT GND SINK TYPE
| TB.PWR3.3 | TB.IOEX6/8.9 | DIGITAL INPUT DRY CONTACT COM
| TB.PWR3.3 | TB.ECU.2 | ECU 0VDC_EXT
| TB.PWR3.3 | TB.DIO.LOC.2 | LOCAL GRN BTN COM
| TB.PWR3.3 | TB.DIO.LOC.4 | LOCAL AMBER BTN COM
| TB.PWR3.3 | TB.DIO.LOC.6 | LOCAL ESTOP COM
| TB.PWR3.3 | TB.DIO.LOC.12 | LOCAL ESTOP NO CONTACT COM
| TB.PWR3.3 | TB.DIO.REM.2 | REMOTE GRN BTN COM
| TB.PWR3.3 | TB.DIO.REM.4 | REMOTE AMB BTN COM
| TB.PWR3.3 | TB.DIO.DUN.2 | DUNGS PRESS HI COM
| TB.PWR3.3 | TB.DIO.DUN.4 | DUNGS PRESS LO COM
| TB.PWR3.3 | TB.DIO.DUN.6 | DINGS PROOF OF CLOSURE COM
| TB.PWR3.3 | K24.XV1100.11 | COM FOR XV1100
| TB.PWR3.3 | K24.XV501.11 | COM FOR XV501
| TB.PWR3.3 | K24.XV909.11 | COM FOR XV501
| TB.PWR3.3 | K120.IGN.11 | COM FOR FIRE ROD
| TB.PWR3.3 | TB.BL24.1 | COM FOR BL24 DIGITAL INPUT
| TB.PWR3.3 | TB.PMP24.1 | COM FOR PMP DIGITAL INPUT
| TB.PWR3.3 | REG1.3 | COM FOR 15VDC REG1
| TB.PWR3.3 | TB.FT132.2 | COM FOR FT132
| TB.PWR3.3 | K24.BMM..11 | COM FOR BMM
| TB.PWR3.3 | K24.R_PLT.11 | COM FOR RED PLT AND ESTOP DI(NO)
120.L | START | END | FUNCTION
| TB.EBOX.1 | F.120EN | POWER TO 24VDC PS AND INTERLOCK
120VAC.EN | START | END | FUNCTION
| F.XV801.1 | TB.XV801.1 | 120L FOR XV801
| F.FCV134.1 | TB.FCV134A.1 | 120L FOR FCV134
| F.FCV141.1 | TB.FCV141A.1 | 120L FOR FCV141A
| F.FCV205.1 | TB.FCV205.1 | 120L FOR FCV205
| F.TWV308.1 | K24.TWV308.11 | 120L FOR TWV308 OPEN/CLOSE
| F.TWV901.1 | K24.TWV901.11 | 120L FOR TWV901 OPEN/CLOSE
120.N | START | END | FUNCTION
| TB.EBOX.2 | TB.PWR3.5 | NEUTRAL FOR 24VDC PS
| TB.EBOX.2 | K24.XV801.11 | NEUTRAL FOR XV801
| TB.EBOX.2 | K24.120EN.11 | NEUTRAL FOR K120EN
| TB.EBOX.2 | TB.FCV.141A.2 | NEUTRAL FOR FCV141
| TB.EBOX.2 | TB.FCV205A.2 | NEUTRAL FOR FCV205
| TB.EBOX.2 | TB.BMM120.2 | NEUTRAL FOR BMM120
| TB.EBOX.2 | TB.TWV308.2 | NEUTRAL FOR TWV308
| TB.EBOX.2 | TB.TWV901.2 | NEUTRAL FOR TWX909

## TERMINAL BLOCKS
Terminal Block Designation
TB.ECU | PIN | END | FUNCTION
| 1 | F.ECU.2 | 24VDC POWER
| 2 | TB.PWR3.3 | 0VDC_EXT
| 3 | SPARE | NC
| 4 | SPARE | NC
| 5 | SPARE | NC
| 6 | TB.BMM.3 | RS485 COMM+
| 7 | TB.BMM.4 | RS485 COMM -
| 8 | SPARE | NC
| 9 | SPARE | NC
| 10 | SPARE | NC
| 11 | SPARE | NC
| 12 | TB.EBOX.7 | CHASSIS GND
TB.DIO.LOC | PIN | END | FUNCTION
| 1 | TB.IOEX6/8.7,TB.DIO.REM.1 | GRN BTN
| 2 | TB.PWR3.3 | COM FOR GRN BTN
| 3 | TB.IOEX6/8.8,TB.DIO.REM.3 | AMB BTN
| 4 | TB.PWR3.3 | COM FOR AMB BTN
| 5 | K24.120EN.A1 | ESTOP INTERLOCK
| 6 | TB.PWR3.3 | 0VDC COM FOR ESTOP
| 7 | F.IOEX7.2 | 24VDC GRN PILOT
| 8 | TB.IOEX7.12,TB.DIO.REM.6 | GRN PILOT DIGITAL OUTPUT
| 9 | F.IOEX7.2 | 24VDC AMB PILOT
| 10 | TB.IOEX7.11,TB.DIO.REM.8 | AMB PILOT DIGITAL OUTPUT
| 11 | TB.IOEX6/8.6,K24.R_PLT.14 | ESTOP DIGTAL INPUT NO
| 12 | NC | SPARE
TB.DIO.REM | PIN | END | FUNCTION
| 1 | TB.IOEX6/8.7/TB.DIO.LOC.1 | GRN BTN REM
| 2 | TB.PWR3.3 | GRN BTN COM
| 3 | TB.IOEX6/8.8,TB.DIO.REM.3 | AMB BTN REM
| 4 | TB.PWR3.3 | AMB BTN COM
| 5 | F.IOEX7.2 | 24VDC GRN PILOT
| 6 | TB.IOEX7.12,TB.DIO.LOC.8 | GRN PILOT OUTPUT
| 7 | F.IOEX7.2 | 24VDC AMB PILOT
| 8 | TB.IOEX7.11,TB.DIO.LOC.10 | AMB PILOT OUTPUT
| 9 | F.IOEX7.2 | 24VDC RED PILOT
| 10 | K24.R_PLT.14 | COM FOR RED PILOT
| 11 | NC | SPARE
| 12 | NC | SPARE
TB.DUN | PIN | END | FUNCTION
| 1 | TB.IOEX6/8.10 | DUNGS PRESSURE HIGH SWITCH
| 2 | TB.PWR3.3 | 0VDC_EXT
| 3 | TB.IOEX6/8.11 | DUNGS PRESSURE LOW SWITCH
| 4 | TB.PWR3.3 | 0VDC_EXT
| 5 | TB.IOEX6/8.12 | DUNGS PROOF OF CLOSURE SWITCH
| 6 | TB.PWR3.3 | 0VDC_EXT
| 7 | TB.EBOX.7 | CHASSIS GND
TB.BMM24 | PIN | END | FUNCTION
| 1 | F.BMM24.1 | 24VDC BM CR2
| 2 | K24.BMM.14 | COM FOR BMM CR2
| 3 | TB.ECU.6 | RS485+
| 4 | TB.ECU.7 | RS485-
| 5 | F.OCI.2 | 24VDC OCI
| 6 | TB.PWR3.3 | OCI 0VDC_EXT COM
| 7 | TB.EBOX.7 | CHASSIS GND
TB.BL24 | PIN | END | FUNCTION
| 1 | TB.PWR3.3 | 0VDC _EXT COM
| 2 | TB.IOEX7.2 | DO9 BL24 FWD
| 3 | TB.IOEX1/2.1 | 0-10VDC AO SIG
| 4 | TB.IOEX1/2.2 | 0-10VDC AO COM
| 5 | TB.IOEX6/8.1 | 4..20mA FB
| 6 | TB.IOEX6/8.2 | 4..20mA FB COM
| 7 | TB.EBOX.7 | CHASSIS GND
TB.PMP24 | PIN | END | FUNCTION
| 1 | TB.PWR3.3 | 0VDC_EXT
| 2 | TB.IOEX7.1 | DO10 PMP24 FWD
| 3 | TB.IOEX1/2.3 | 0-10VDC AO SIG
| 4 | TB.IOEX1/2.4 | 0-10VDC AO COM
| 5 | TB.IOEX6/8.3 | 4..20mA FB
| 6 | TB.IOEX6/8.4 | 4..20mA FB COM
| 7 | TB.EBOX.7 | CHASSIS GND
TB.PT213 | PIN | END | FUNCTION
| 1 | F.PT.2 | 24VDC
| 2 | TB.IOEX6.7 | PT213.FB.SIG
| 3 | TB.EBOX.7 | CHASSIS GND
TB.PT420 | PIN | END | FUNCTION
| 1 | F.PT.2 | 24VDC
| 2 | TB.IOEX6.5 | PT420.FB.SIG
| 3 | TB.EBOX.7 | CHASSIS GND
TB.PT304 | PIN | END | FUNCTION
| 1 | F.PT.2 | 24VDC
| 2 | TB.IOEX6.3 | PT304.FB.SIG
| 3 | TB.EBOX.7 | CHASSIS GND
TB.PT318 | PIN | END | FUNCTION
| 1 | F.PT.2 | 24VDC
| 2 | TB.IOEX6.9 | PT318.FB.SIG
| 3 | TB.EBOX.7 | CHASSIS GND
TB.XV1100 | PIN | END | FUNCTION
| 1 | F.XV1100 | 24VDC
| 2 | K24.XV1100.14 | 0VDC_EXT COM
| 3 | TB.EBOX.7 | CHASSIS GND
TB.XV501 | PIN | END | FUNCTION
| 1 | F.XV501 | 24VDC
| 2 | K24.XV501.14 | 0VDC_EXT COM
| 3 | TB.EBOX.7 | CHASSIS GND
TB.XV909 | PIN | END | FUNCTION
| 1 | F.XV909 | 24VDC
| 2 | K24.XV9009.14 | 0VDC_EXT COM
| 3 | TB.EBOX.7 | CHASSIS GND
TB.FVC141B | PIN | END | FUNCTION
| 1 | TB.IOEX1/2.9 | 0-10VDC AO SIG
| 2 | TB.IOEX1/2.10 | 0-10VDC AO COM
| 3 | TB.EBOX.7 | CHASSIS GND
TB.FVC134B | PIN | END | FUNCTION
| 1 | TB.IOEX6.1 | 4..20mA FB
| 2 | TB.IOEX6.2 | 4..20mA FB COM
| 3 | TB.IOEX1/2.9 | 2-10VDC AO SIG
| 4 | TB.IOEX1/2.10 | 2-10VDC AO COM
| 5 | NC | NC
| 6 | NC | NC
| 7 | TB.EBOX.7 | CHASSIS GND
TB.FT132 | PIN | END | FUNCTION
| 1 | F.15VDC.2 | 15VDC_INT
| 2 | TB.PWR3.3 | 0VDC_EXT
| 3 | TB.IOEX6.11 | 4..20mA FB
| 4 | TB.IOEX6.12 | 4..20mA FB COM
TB.IGN | PIN | END | FUNCTION
| 1 | F.IGN.2 | 24VDC
| 2 | K120.IGN.3 | 0VDC _EXT COM
| 3 | TB.EBOX.7 | CHASSIS GND
TB.XV801 | PIN | END | FUNCTION
| 1 | F.XV801 | 120VAC
| 2 | K24.XV801.14 | NEUTRAL COM
| 3 | TB.EBOX.7 | CHASSIS GND
TB.FCV134A | PIN | END | FUNCTION
| 1 | F.FCV134.2 | 120VAC
| 2 | TB.EBOX.2 | NEUTRAL COM
| 3 | TB.EBOX.7 | CHASSIS GND
TB.FCV141A | PIN | END | FUNCTION
| 1 | F.FCV141.2 | 120VAC
| 2 | TB.EBOX.2 | NEUTRAL COM
| 3 | TB.EBOX.7 | CHASSIS GND
TB.FCV205 | PIN | END | FUNCTION
| 1 | F.FCV205.2 | 120VAC
| 2 | TB.EBOX.2 | NEUTRAL COM
| 3 | TB.IOEX1/2.7 | 0-10VDC AO SIG
| 4 | TB.IOEX1/2.8 | 0-10VDC AO COM
| 5 | NC | NC
| 6 | NC | NC
| 7 | TB.EBOX.7 | CHASSIS GND
TB.BMM120 | PIN | END | FUNCTION
| 1 | F.BMM120.2 | 120VAC
| 2 | TB.EBOX.2 | NEUTRAL COM
| 3 | K120.IGN.5 | 0-10VDC AO SIG
| 4 | K120.IGN.1 | 0-10VDC AO COM
| 5 | NC | NC
| 6 | NC | NC
| 7 | TB.EBOX.7 | CHASSIS GND
TB.TWV308 | PIN | END | FUNCTION
| 1 | K24.TWV308.14 | OPEN
| 2 | TB.EBOX.2 | NEUTRAL COM
| 3 | K24.TWV308.12 | CLOSE
| 4 | TB.EBOX.7 | CHASSIS GND
TB.TWV901 | PIN | END | FUNCTION
| 1 | K24.TWV901.14 | OPEN
| 2 | TB.EBOX.2 | NEUTRAL COM
| 3 | K24.TWV901.12 | CLOSE
| 4 | TB.EBOX.7 | CHASSIS GND
TB.EBOX | PIN | END | FUNCTION
| 1 | F.120EN.1 | 120VAC FROM EBOX
| 2 | TB.EBOX.2 | NEUTRAL COM
| 3 | F.120EN.2 | SPARE
| 4 | TB.EBOX.7 | CHASSIS GND

## RELAYS
24VDC COILS
K24.BMM
| PIN | END | FUNCTION
| A1 | TBIOEX7.3 | DO8
| A2 | F.COILS.2 | 24VDC
| 11 | TB.PWR3.3 | 0VDC_EXT COM
| 12 | NC | NC
| 14 | TB.BMM24.2 | CR2 COM
K24.XV1100
| PIN | END | FUNCTION
| A1 | TB.IOEX7.7 | DO4
| A2 | F.COILS.2 | 24VDC
| 11 | TB.PWR3.3 | 0VDC_EXT COM
| 12 | NC | NC
| 14 | TB.XV1100.1 | ACT XV1100
K24.XV501
| PIN | END | FUNCTION
| A1 | TB.IOEX7.9 | DO3
| A2 | F.COILS.2 | 24VDC
| 11 | TB.PWR3.3 | 0VDC_EXT COM
| 12 | NC | NC
| 14 | TB.XV501.2 | ACT XV501
K24.XV909
| PIN | END | FUNCTION
| A1 | TB.IOEX7.10 | DO2
| A2 | F.COILS.2 | 24VDC
| 11 | TB.PWR3.3 | 0VDC_EXT COM
| 12 | NC | NC
| 14 | TB.XV909.2 | ACT XV909
K24.TWV308
| PIN | END | FUNCTION
| A1 | TB.IOEX7.5 | DO6
| A2 | F.COILS.2 | 24VDC
| 11 | F.TWV308.2 | 120VAC
| 12 | TB.TWV308.3 | CLOSE
| 14 | TB.TWV308.1 | OPEN
K24.TWV901
| PIN | END | FUNCTION
| A1 | TB.IOEX7.4 | DO7
| A2 | F.COILS.2 | 24VDC
| 11 | F.TWV901.2 | 120VAC
| 12 | TB.TWV901.3 | CLOSE
| 14 | TB.TWV901.1 | OPEN
K24.XV801
| PIN | END | FUNCTION
| A1 | TBIOEX7.6 | DO5
| A2 | COILS.24 | 24VDC
| 11 | TB.EBOX.2 | NEUTRAL COM
| 12 | NC | NC
| 14 | TB.XV801.2 | XV801 ACT
K24.120EN
| PIN | END | FUNCTION
| A1 | TB.DIO.LOC.5 | ESTOP NC INTERLOCK
| A2 | COILS.24 | 24VDC
| 11 | TB.EBOX.2 | NEUTRAL COM
| 12 | NC | NC
| 14 | K120.EN.5 | K120.EN SINK
K24.R_PLT
| PIN | END | FUNCTION
| A1 | TB.DIO.LOC.5 | ESTOP NC INTERLOCK
| A2 | COILS.24 | 24VDC
| 11 | TB.PWR3.3 | 0VDC_EXT COM
| 12 | TB.DIO.REM.10 | LAMP OFF
| 14 | TB.DIO.LOC.5 | DIGITAL INPUT ESTOP
120VAC COILS
K120.EN | PIN | END | FUNCTION
| 1 | F.120EN.2 | 120VAC
| 2 | NC | NC
| 3 | 120VAC.EN | 120 L TO FUSE BUS
| 4 | TB.EBOX.1 | 120 L FROM EBOX
| 5 | K24.120EN.14 | NEUTRAL COM
K120.IGN | PIN | END | FUNCTION
| 1 | TB.BMM120.4 | NEUTRAL SIGNAL
| 2 | NC | NC
| 3 | TB.IGN.2 | OVDC COM
| 4 | TB.PWR3.3 | 0VDC_EXT COM
| 5 | TB.BMM120.3 | LOAD SIGNAL

## FUSES
FUSES
24VDC FUSES
F.ECU
| PIN | END | FUNCTION
| 1 | TB.PWR3.4 | 24VDC
| 2 | TB.ECU.1
F.ETHSW
| PIN | END | FUNCTION
| 1 | TB.PWR3.4 | 24VDC
| 2 | TB.PWR2.5
F.IOEX1
| PIN | END | FUNCTION
| 1 | TB.PWR3.4 | 24VDC
| 2 | TB.PWR1.12
F.IOEX2
| PIN | END | FUNCTION
| 1 | TB.PWR3.4 | 24VDC
| 2 | TB.PWR1.10
F.IOEX3
| PIN | END | FUNCTION
| 1 | TB.PWR3.4 | 24VDC
| 2 | TB.PWR1.8
F.IOEX4
| PIN | END | FUNCTION
| 1 | TB.PWR3.4 | 24VDC
| 2 | TB.PWR1.6
F.IOEX5
| PIN | END | FUNCTION
| 1 | TB.PWR3.4 | 24VDC
| 2 | TB.PWR1.4
F.IOEX6
| PIN | END | FUNCTION
| 1 | TB.PWR3.4 | 24VDC
| 2 | TB.PWR1.2
F.IOEX7
| PIN | END | FUNCTION
| 1 | TB.PWR3.4 | 24VDC
| 2 | TB.PWR2.11,TB.DIO.LOC.7,TB.DIO.LOC.9,TB.DIO.REM.5,TB.DIO.REM.7,TB.DIO.REM.9
F.IOEX8
| PIN | END | FUNCTION
| 1 | TB.PWR3.4 | 24VDC
| 2 | TB.PWR2.8,TB.IOEX6/8.5
F.BMM24
| PIN | END | FUNCTION
| 1 | TB.PWR3.4 | 24VDC
| 2 | TB.BMM24.1
F.XV1100
| PIN | END | FUNCTION
| 1 | TB.PWR3.4 | 24VDC
| 2 | TB.XV1100.1
F.XV501
| PIN | END | FUNCTION
| 1 | TB.PWR3.4 | 24VDC
| 2 | TB.XV501.1
F.XV909
| PIN | END | FUNCTION
| 1 | TB.PWR3.4 | 24VDC
| 2 | TB.XV909.1
F.COILS
| PIN | END | FUNCTION
| 1 | TB.PWR3.4 | 24VDC
| 2 | COILS.24
F.PT
| PIN | END | FUNCTION
| 1 | TB.PWR3.4 | 24VDC
| 2 | TB.PT213.1,TB.PT420.1,TB.PT304.1,TB.PT318.1
F.OCI
| PIN | END | FUNCTION
| 1 | TB.PWR3.4 | 24VDC
| 2 | TB.BMM24.5,REG1
F.IGN
| PIN | END | FUNCTION
| 1 | TB.PWR3.4 | 24VDC
| 2 | TB.IGN.1
F.15VDC
| PIN | END | FUNCTION
| 1 | REG1.2 | 15VDC
| 2 | TB.FT132.1 | FT132 +V
F.XV801
| PIN | END | FUNCTION
| 1 | K120VAC.EN.3 | 120VAC ENA
| 2 | TB.XV801.1 | VAC FOR COIL
F.FCV134
| PIN | END | FUNCTION
| 1 | K120VAC.EN.3 | 120VAC ENA
| 2 | TB.FCV134A.1 | 120L FCV134
F.FCV141
| PIN | END | FUNCTION
| 1 | K120VAC.EN.3 | 120VAC ENA
| 2 | TB.FCV141A.1 | 120L FCV141
F.FCV205
| PIN | END | FUNCTION
| 1 | K120VAC.EN.3 | 120VAC ENA
| 2 | TB.FCV205.1 | 120L FCV205
F.BMM120
| PIN | END | FUNCTION
| 1 | K120VAC.EN.3 | 120VAC ENA
| 2 | TB.BMM120.1,TB.EBOX.4 | 120 VAC BMM, TB.EBOX.4
F.TWV308
| PIN | END | FUNCTION
| 1 | K120VAC.EN.3 | 120VAC ENA
| 2 | K24.TWV308.11 | 120VAC TWV308
F.TWV901
| PIN | END | FUNCTION
| 1 | K120VAC.EN.3 | 120VAC ENA
| 2 | K24.TWV901.11 | 120VAC TWV901
F.120EN
| PIN | END | FUNCTION
| 1 | K120VAC.EN.3 | 120VAC ENA
| 2 | K120.EN.1,TB.PWR3.Y6 | 120VAC PS24VDC, 120 EN